## Sheet1
Life Safety Monthly Checklist
PLACE A CHECKMARK IN APPROPRIATE BOX TO DOCUMENT COMPLIANCE STATUS. Add comments for any non-compliance or special condition.
DATE: LOCATION: | Compliant | Not Compliant | Comments
Name:
Date of last fire drill:
Are all escape pathways in the home continuously maintained free of obstructions or impediments?
Does each story of the home have two remotely located means of escape (such as exterior doors or stairways) that don't require using windows?
Are all doors operable from the egress side without a key, tool or special knowledge? All doors must have lever handle single action locks
Are doors free of obstruction and/or free from wedges holding doors open?
Do all doors close properly, latch and free of furniture that would prevent the individual from closing the bedroom door?
Has a functional emergency lighting test been conducted monthly at intervals for not less than 30 seconds, and an annual test of all battery powered emergency lighting for not less than one and a half hours?
If emergency lighting system is not fully operational for the duration of the test, have batteries been replaced?
Are all Fire Extinguishers within current date of inspection? Must be checked monthly, initialed & dated
Are all portable fire extinguishers inspected annually in accordance with the NFPA?
All fire extinguishers & pull stations unobstructed?
Has a fire marshall performed inspection annually? Is report in state binder?
Is there a written contract with the fire alarm firm in the state binder?
Are the fire alarm inspections performed semi-annually?
Has a smoke detector sensitivity test been performed within one year after installation and every alternate year thereafter?
Is the smoke detector sensitivty report in the state binder?
Is there a copy of a contract for a fire protection sprinkler maitenence service in the state binder?
Are services for sprinkler system inspections performed semi-annually?
Has backflow preventer testing been performed annually and a copy of report in state binder?
Has Range Hood Fire Suppression System been checked semi-annually and a report in state binder?
Has Range Hood cleaning been performed semi-annually or as needed?
Is an emergency generator onsite?
Has the emergency generator been inspected weekly and excercised underload at least monthly for a minimum of 30 minutes at not less than 30% of the emergency generator nameplate rating?
Have fire drills been conducted quarterly on each shift and with at least one drill conducted each month?
Are smoking ash trays/tower made of noncombustible material? (metal)
Have all curtains and window valences been treated with a flame-resistant product?
Is there a gas line pressure test documented and in the state binder?
Has gas heating system been checked annually prior to the heating season?
Are all stored items 6" from ceiling or greater in resident rooms, closets and pantries?
Is there at least one manual pull station in the home?
Does the home have adequate, fully charged ABC fire extinguishers within 75 feet of any location in the home?
Do labels on the fire extinguishers indicate that staff inspect the extinguishers monthly and an authorized person is inspecting the extinguishers annually?
If there are electrical receptacles located within 6 feet of the edge of a sink, do the receptacles have ground - fault circuit interrupter (GFCI) protection?
Are all circuits labeled at the main electrical panel?
Does the home have a written emergency plan for protecting all persons in the event of a fire?
Have individuals in the home received training in the proper actions to be taken in the event of a fire?
Is the Smoking Policy posted?
Are evacuation routes posted at entry and exit doors, including all resident rooms?
Do you have a copy of your disaster relocation to include name and address of location?
Locate & note location of water shut off for each house
Are emergency manuals in proper location and accessible to staff?
Is Disaster Plan up to date?
Is Staff Roster up to date with proper staff names and phone numbers?
Is chain of command posted and up to date?
Are there copies of the schedule accessible and available for the last 12 months?
Are there weekly copies of the food menu for a total of 12 months available and accessible?
Are refrigerator temperatures recorded daily and reports available and accessible for 12 months?
Are freezer temperatures recorded daily and reports available and accessible for 12 months?
Are medication refrigerator temperatures recorded daily and reports available and accessible for 12 months?
Are pest control service documents available for each service?